## IP
id | name | com_type | ip_address | port | period | wait_time | active
1 | VAV(교실1) | tcp/ip | 192.168.0.151 | 502 | 200 | 2000 | 1
Note on A1: auto increment
Note on B1: unique

## Channel
id | name | channel_id | function_code | device_address | start_address | read_byte | active
1 | 교실-1 | 1 | 3 | 1 | 1 | 1 | 1
Note on H1: 0 : 실행하지 않음 1 : 실행함

## DATA
ObjectName | ObjectType | id | Units | Low Limit | High Limit | M_Enable | M_IP | M_Channel | M_Func | M_Addr | M_OffsetBit | M_DatType | M_R_Scale | M_R_Offset | M_W_IP | M_W_ID | M_W_FC | M_W_Addr | M_W_DatType | M_W_Scale | M_W_Offset
교실-1 실내온도 | AI | 1 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 1 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 실내습도 | AI | 2 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 2 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 이산화탄소 | AI | 3 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 3 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 미세먼지 PM2.5 | AI | 4 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 4 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 미세먼지 PM10 | AI | 5 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 5 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 재실동작 | AI | 6 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 6 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 외기온도 | AI | 7 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 7 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 외기습도 | AI | 8 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 8 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 외기CO2 | AI | 9 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 9 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 외기 PM2.5 | AI | 10 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 10 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 외기 PM10 | AI | 11 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 11 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 급기풍량 | AI | 12 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 12 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 환기풍량 | AI | 13 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 13 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 급기덕트정압 | AI | 14 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 14 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 VAV MAN/AUTO | AI | 15 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 15 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
교실-1 VAV ACTION | AI | 16 | Bar | 0 | 999999999 | 1 | 1 | 1 | 3 | 16 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0
Note on B1: OBJECT TYPE: AI/AO/ACC BI/BO MI/MO/MV
Note on C1: OBJ INSTANCE NO: [ISSNO][MIDNO][PIDNO] - ISSNO ; 0-239 - MIDNO ; 0-31 - PIDNO ; 0-23
Note on G1: MODBUS/TCP [Point Enable] 0 : Disable 1 : Enable (Default)
Note on H1: MODBUS/TCP-IP [Read Modbus IP] 0 : 할당없음 (Default) 1~99 : 통신 채널 번호
Note on I1: MODBUS/TCP [Read Modbus Channel] 0 : 할당없음 (Default) 1~64 : 통신 프레임 번호
Note on J1: MODBUS/TCP [Read Modbus Funcl] 00 : Read Coils 01 : Read Discrete Input 03 : Read Holding Registers 04 : Read Input Registers
Note on K1: MODBUS/TCP [Read Modbus X Ref Address] 0 : 할당없음 1~9999 : 모드버스 X 주소번지 (십진법)
Note on L1: MODBUS/TCP [Read Bit Offset] 0~15 : 비트 옵셋 위치 (Default:0) 현재 관제점 시작 메모리 위치에서 비트 옵셋 위치 (데이터 타입이 bit 형일 경우에만 의미 있음)
Note on M1: MODBUS/TCP [Read Data Type] 00 : Uint16-AB 01 : Int16 02 : Int32-AB CD 03 : Int32-CD AB 04 : Int32-BA DC 05 : Int32-DC BA 06 : Float-AB CD 07 : Float-CD AB 08 : Float-BA DC 09 : Float-DC BA 10 : Double-AB CD EF GH 11 : Double-GH EF CD AB 12 : Double-BA DC FE HG 13 : Double-HG FE DC BA 14 : 1bit value (0/1)
Note on N1: MODBUS/TCP [Read Scale] Point Value = Point Value * Scale Value (Default : 1.0)
Note on O1: MODBUS/TCP [Read Offset] Point Value = Point Value + Offset Value (Default : 0.0)
Note on P1: MODBUS/TCP [Write Channel] MODSetup 채널번호 : 1~100 (디폴트0)
Note on Q1: MODBUS/TCP [Write Device ID] MODSetup 쓰기장치번호 : 1~255 (디폴트 : 0)
Note on R1: MODBUS/TCP [Write Func Addr] 05 : Write Single coil (AO) 06 : Write Single Register(BO)
Note on S1: MODBUS/TCP [Write Point Addr] MODSetup 관제점주소 (Coil) 1~9999 (Default) 0
Note on T1: MODBUS/TCP [Read Data Type] 00 : Uint16-AB 01 : Int16 02 : Int32-AB CD 03 : Int32-CD AB 04 : Int32-BA DC 05 : Int32-DC BA 06 : Float-AB CD 07 : Float-CD AB 08 : Float-BA DC 09 : Float-DC BA 10 : Double-AB CD EF GH 11 : Double-GH EF CD AB 12 : Double-BA DC FE HG 13 : Double-HG FE DC BA 14 : 1bit value (0/1)
Note on U1: MODBUS/TCP [Write Scale] Write Value = Write Value * Scale Value (Default : 1.0)
Note on V1: MODBUS/TCP [Write Offset] Write Value = Write Value + Offset Value (Default : 0.0)

## help
Tag Type
화재
조명
전력량
온도
시스템에어컨
습도
수도량
pm25
pm10
이산화탄소